Master MPS
MPM 10
INPUT		
Voltage	380 / 400 / 415 V three-phase 	
Frequency	45 - 65 Hz 	
Frequency tolerance	±2% (selectable from ±1% to ±5% from front panel)	
Soft start	0 - 100% in 120 sec (selectable)	
Voltage Range	400 V +20% -25% 	
BY PASS		
Rated voltage	220 / 230/ 240 V single-phase + N	
Rated frequency	50 or 60 Hz (selectable) 	
OUTPUT and INVERTER OUTPUT		
Rated power	10000 VA	
Active power	9000 W	
Output Voltage	220 / 230 / 240 V single-phase + N (selectable) 	
Crest factor (Ipeak/Irms)	3 : 1 	
Static stability	±1% 	
Dynamic stability	±5% in 10 ms 	
Frequency	50 or 60 Hz (selectable) 	
Voltage distortion with non-linear load	<3% 	
Voltage distortion with linear load	<1% 	
Frequency stability	0.05% 	
Overload	110% for 60 min.; 125% for 10 min.; 150% for 1 min. 	
BATTERIES		
Type	VRLA AGM / GEL; NiCd; Supercaps; Li-ion; Flywheels 	
ENVIRONMENTAL		
Color	Dark grey RAL 7016 	
Communication	Double RS232 + dry contacts + 2 slots for communications interface 	
Protection rating	IP20 	
Line-Interactive/Smart Active efficiency	Up to 98% 	
Noise	60 [dBA±2] (ECO Mode) 	
Operating temperature	0 °C - +40 °C	
Relative humidity	5-95% non-condensing	
Standards	European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive and Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight	200 kg	
Dimensions (h w d)	1400x555x740 mm