Multi Sentry
MST 30
INPUT		
Rated power	30000 VA	
Voltage	380 / 400 / 415 V three-phase + N 	
Voltage tolerance	400 V ±20% @ full load (For wider tolerance conditions apply) 	
Frequency tolerance	40 - 72 Hz	
Power factor	0.99	
BY PASS		
Rated voltage	380 / 400 / 415 V three-phase + N	
Rated frequency	50 or 60 Hz (selectable) 	
Frequency tolerance	±5% (selectable) 	
Number phases	3 + N 	
OUTPUT and INVERTER OUTPUT		
Rated power	30000 VA	
Active power	27000 W	
Number phases	3 + N 	
Crest factor (Ipeak/Irms)	3 : 1 	
Static stability	±1% 	
Dynamic stability	±3% 	
Frequency	50 or 60 Hz 	
Voltage distortion with non-linear load	≤3% 	
Voltage distortion with linear load	≤1% 	
BATTERIES		
Type	VRLA AGM/GEL/NiCd/Li-ion/Supercaps 	
Recharge time	6 h 	
ENVIRONMENTAL		
Color	Dark grey RAL 7016 	
Communication	3 slots for communications interface / USB / RS232 	
Protection rating	IP20 	
Line-Interactive/Smart Active efficiency	Up to 99% 	
Noise	<40 [dBA±2] (SMART ACTIVE) 	
Remote signals	voltage free contacts	
Operating temperature	0 °C - +40 °C	
Relative humidity	5-95% non-condensing	
Standards	European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive and Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight	135 kg	
Dimensions (h w d)	1320x440x823 mm