Master HP UL
MHT 65 UL
INPUT		
Voltage	480 V three-phase + N 	
Frequency	45 / 65 Hz 	
Frequency tolerance	±2% (selectable from ±1% to ±5% from front panel)	
Power factor	>0.99	
Current distorsion	<3% THDi	
Soft start	0 - 100% in 125” (selectable)	
OUTPUT and INVERTER OUTPUT		
Rated power	65000 VA	
Active power	58500 W	
Number phases	3 + N 	
Crest factor (Ipeak/Irms)	3:1  	
Waveform (Battery Mode)	Sinusoidal 	
Static stability	±1% 	
Dynamic stability	from ±5% to ±1% in 20 msec. 	
Frequency	60 Hz 	
Frequency on battery operation	0.05% 	
Frequency stability	0.05% 	
Overload	110% for 60 min.; 125% for 10 min.; 150% for 1 min. 	
RECTIFIER OUTPUT		
Ripple	Zero	
BATTERIES		
Type	VRLA, Wet Cell, NiCd 	
ENVIRONMENTAL		
Color	Black 	
Remote controls	ESD and bypass (configurable) 	
Communication	Double RS232 + dry contacts + 2 slots for communications interface with SNMP, Modbus, and Bacnet Protocols 	
Protection rating	IP20  	
Marks	UL 	
Other compliances	UL Standard 1778: 2nd ed. from 65 to 125 kVA, 5th ed. from 160 to 250 kVA; From 160 to 250 kVA: UL 60950-1 1 - Safety - Part 1: General National Electrical Code (NFPA-70); FCC Part 15 Subpart J class A - IEC 62040-3; UL 924 and OUST category  	
Line-Interactive/Smart Active efficiency	up to 98.5% 	
Noise	65 dBA 	
Remote signals	dry contacts (configurable)	
Operating temperature	32 – 104 °F / 0 – 40 °C	
Relative humidity	<95% non-condensing	
Transport	Pallet jack 	
Power loss at 100% load	15024 BTU/h 	
DATA		
Weight	1500 lbs / 680 kg	
Dimensions (h w d)	75 x 31.50 x 33.50 inches / 1900 x 800 x 850 mm