Master HE
MHE 100
INPUT		
Voltage	380 / 400 / 415 V 3-phase 	
Voltage tolerance	400 ±20% @ full load 	
Frequency	45 - 65 Hz 	
Frequency tolerance	±2% (selectable from ±1% to ±5% from front panel)	
Power factor	>0.99	
Soft start	0 - 100% in 120 sec. (selectable)	
Total harmonic distortion (THDi)	<3% 	
BY PASS		
Rated voltage	380 / 400 / 415 V 3-phase + N	
Number phases	3 	
OUTPUT and INVERTER OUTPUT		
Rated power	100000 VA	
Active power	100000 W	
Number phases	3 + N 	
Crest factor (Ipeak/Irms)	3:1 	
Static stability	 ±1% 	
Dynamic stability	±5% in 10 msec. 	
Frequency	50 or 60 Hz (selectable) 	
Frequency on battery operation	 0.05% 	
Voltage distortion with non-linear load	<3% 	
Voltage distortion with linear load	<1% 	
Overload	110% for 60 min.; 125% for 10 min.; 150% for 1 min. 	
RECTIFIER OUTPUT		
Ripple	Zero	
BATTERIES		
Type	VRLA AGM / GEL; NiCd; Supercaps; Li-ion; Flywheels 	
ENVIRONMENTAL		
Color	Dark grey RAL 7016 	
Remote controls	ESD and bypass (configurable) 	
Communication	 Double RS232 + remote contacts + 2 slots for communications interface 	
Protection rating	IP20 (others upon request) 	
Line-Interactive/Smart Active efficiency	>99% 	
Noise	63 - 68 dBA  	
Remote signals	volt-free contacts (configurable)	
Operating temperature	0 °C - +40 °C	
Relative humidity	5-95% non-condensing	
Standards	European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive and Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight	850 kg	
Dimensions (h w d)	1900x800x850 mm