Sentinel Rack
SER 1500 A5
INPUT		
Rated power	1500 VA	
Voltage	220 / 230 / 240 V 	
Voltage tolerance	230 V ±20% 	
Frequency	50 / 60 Hz 	
Frequency tolerance	50 Hz ±5% / 60 Hz ±5%	
Power factor	>0.99	
Current distorsion	≤7%	
BY PASS		
Voltage tolerance	180 / 264 V 	
Frequency tolerance	Frequency selected (from ±1.5 Hz to ±5 Hz configurable) 	
OUTPUT and INVERTER OUTPUT		
Rated power	1500 VA	
Active power	1350 W	
Number phases	1 	
Crest factor (Ipeak/Irms)	3 : 1 	
Waveform (Battery Mode)	Sinusoidal 	
Frequency	Selectable: 50 Hz or 60 Hz or self-learning 	
Voltage distortion with non-linear load	<4% 	
Voltage distortion with linear load	<2% 	
OVERLOAD TIMES		
Load = 150%	1 sec. 	
Load = 125%	5 sec. 	
BATTERIES		
Type	VRLA AGM maintenance-free lead based 	
Recharge time	2-4 h 	
ENVIRONMENTAL		
Color	Black 	
Communication	USB / DB9 with RS232 and contacts / Slot for communications interface 	
Accessories provided	Power cable, IEC-IEC cable, USB cable, safety manual, quick start guide 	
Surge capability	300 J 	
Marks	CE 	
Protections	Overcurrent - short circuit - overvoltage - undervoltage - temperature - excessive low battery	
Line-Interactive/Smart Active efficiency	98% 	
Noise	<40 [bBA] (ECO Mode) 	
Operating temperature	0 °C - +40 °C	
Relative humidity	5-95% non-condensing	
Output sockets	8 IEC 320 C13 	
Standards	European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive and Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight	22 kg	
Dimensions (h w d)	87x450x380 (2Ux19"x380) mm