Sentinel Rack
SER 1500 A5
INPUT |
Rated power | 1500 VA
Voltage | 220 / 230 / 240 V
Voltage tolerance | 230 V ±20%
Frequency | 50 / 60 Hz
Frequency tolerance | 50 Hz ±5% / 60 Hz ±5%
Power factor | >0.99
Current distorsion | ≤7%
BY PASS |
Voltage tolerance | 180 / 264 V
Frequency tolerance | Frequency selected (from ±1.5 Hz to ±5 Hz configurable)
OUTPUT and INVERTER OUTPUT |
Rated power | 1500 VA
Active power | 1350 W
Number phases | 1
Crest factor (Ipeak/Irms) | 3 : 1
Waveform (Battery Mode) | Sinusoidal
Frequency | Selectable: 50 Hz or 60 Hz or self-learning
Voltage distortion with non-linear load | <4%
Voltage distortion with linear load | <2%
OVERLOAD TIMES |
Load = 150% | 1 sec.
Load = 125% | 5 sec.
BATTERIES |
Type | VRLA AGM maintenance-free lead based
Recharge time | 2-4 h
ENVIRONMENTAL |
Color | Black
Communication | USB / DB9 with RS232 and contacts / Slot for communications interface
Accessories provided | Power cable, IEC-IEC cable, USB cable, safety manual, quick start guide
Surge capability | 300 J
Marks | CE
Protections | Overcurrent - short circuit - overvoltage - undervoltage - temperature - excessive low battery
Line-Interactive/Smart Active efficiency | 98%
Noise | <40 [bBA] (ECO Mode)
Operating temperature | 0 °C - +40 °C
Relative humidity | 5-95% non-condensing
Output sockets | 8 IEC 320 C13
Standards | European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive and Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111
DATA |
Weight | 22 kg
Dimensions (h w d) | 87x450x380 (2Ux19"x380) mm

© RPS Spa - Member of the Riello Elettronica Group - VAT IT02647040233 - Fully paid-up share capital: € 1.230.278,00 - Business Register Verona: N° REA 252286