Multi Power
MPX 75 (MPX 130 PWC)
OVERALL SPECIFICATION		
Cabinet type	MPX 130 PWC Power Cabinet 	
Power Module nominal power (Named PM)	15 kW	
Solution nominal Power	75 kW	
Output power factor [pf]	1 	
Parallelable (up to)	4 	
Cabinet layout description	5 x MPX 15 PM 	
INPUT		
Rated power	75000 VA	
Voltage	380 / 400 / 415 V three-phase + N 	
Frequency tolerance	40 - 72 Hz	
Power factor	1	
BY PASS		
Rated voltage	380 / 400 / 415 V three-phase + N	
OUTPUT and INVERTER OUTPUT		
Rated power	75000 VA	
Active power	75000 W	
Number phases	3 	
Output Voltage	380 / 400 / 415 V three-phase + N 	
Dynamic stability	EN62040-3 class performance 1 non linear load 	
Frequency	50 or 60 Hz 	
MODULAR BATTERIES		
Battery Cabinet Type	Modular Type (MPW 170 BTC) 	
Layout	Modular type made up by Battery Unit (named BU) 	
Battery features	VRLA batteries lined up inside BU; Constant voltage and current measuring at BU level; Battery status monitoring via Multi Power LCD display 	
Cabinet lay out description	9 x Battery shelves 	
Dimensions (h w d)	2000x600x1050 mm	
Weight (without PM / BU )	280 kg	
CONVENTIONAL BATTERIES		
Battery Cabinet Type	Conventional Type  	
Layout	Free Standing Battery cabinet / Shelf 	
Battery features	Conventional battery Blocks VRLA Type 	
Cabinet lay out description	1 x (20 + 20) Blocks 	
Dimensions (h w d)	2000x860x800 mm	
Weight (without PM / BU )	250 kg	
ENVIRONMENTAL		
Color	RAL 9005 	
Protection rating	IP20 finger proof (either with cabinet doors open or close) 	
Noise	<65 [dBA±2] 	
Standards	European directives: L V 2014/35/EU low voltage; EMC 2014/30/EU electromagnetic compatibility -- Directive & Standards: Safety IEC EN 62040-1; EMC IEC EN 62040-2 - category C2; RoHS compliant -- Classification in accordance with IEC 62040-3 VFI - SS - 111 	
DATA		
Weight	145 kg	
Dimensions (h w d)	1200x600x1050 mm	
Input phases	3 	
Output phases	3